TEST CERTIFICATE

TC NO: AFPL/2026-27/4283                                                                                                                  DATE: 2026-09-30

CLIENT NAME: MACLEODS PHARMACEUTICALS LIMITED - PALGHAR PLANT

CLIENT PO NO: - PO-4500020105	                                                                               PO DATE: 2026-08-18

FILTER SERIAL NUMBER:  AFPL/202627/EU04/11666 TO 11677                                         TESTING DATE: 2026-09-28

EQUIPMENT USED FOR TESTING: 2026-09-28

| MANUFACTURER: - AIRFIL FILTECH PVT. LTD. |  |  |  |  |
| --- | --- | --- | --- | --- |
| TYPE OF FILTER: PRE FILTER - 20 MICRON (BOX TYPE) |  |  |  |  |
| PRODUCT DETAILS |  |  |  |  |
| FILTER MEDIA | FILTER CAPACITY | FILTER DIMEMSION |  | MOC |
| HDPE + Non-Woven Synthetic Media + HDPE Supported By Al Rod | 201 CFM | 400 X 170 X 25MM |  | ALUMINIUM |
| AIR FLOW RATE | INITIAL PRESSURE DROP | FINAL PRESSURE DROP |  | TEMPERATURE |
| 201 CFM | 20 - 30 Pa | 150 Pa |  | AMBIENT |
| TEST DATA |  |  |  |  |
| TEST AIRFLOW | AIR VELOCITY |  | AIR TEMPERATURE |  |
| 250 FPM | 25 °C |  | 25 °C |  |
| TEST RESULT |  |  |  |  |
| INITIAL PRESSURE DROP (Pa) | EFFCIENCY |  | FILTER CLASS |  |
| 20 ± 5 % | 85% DOWN TO 20 MICRON |  | EU 04 |  |
| TEST TYPE: BS EN 779 |  |  |  |  |
| INSPECTED BY For Queries Related To TC Please Contact – quality@airfil.in Authorised Signatory |  |  |  |  |