TEST CERTIFICATE

TC NO: 
                                                                                                                         DATE:

CLIENT NAME:

CLIENT PO NO: - 12345	                                                                                        PO DATE: 2026-07-14

FILTER SERIAL NUMBER:  SER/001                                           TESTING DATE: 2026-07-14

EQUIPMENT USED FOR TESTING: 2026-07-14

| MANUFACTURER: - AIRFIL FILTECH PVT. LTD. |  |  |  |  |
| --- | --- | --- | --- | --- |
| TYPE OF FILTER: FINE FILTER -- 3 MICRON (FLANGE TYPE) |  |  |  |  |
| PRODUCT DETAILS |  |  |  |  |
| FILTER MEDIA | FILTER CAPACITY | FILTER DIMEMSION |  | MOC |
| HDPE + NON-WOVEN SYNTHETIC MEDIA + HDPE | 2000 CFM | 610 X 610 X 305 MM |  | ALUMINIUM |
| AIR FLOW RATE | INITIAL PRESSURE DROP | FINAL PRESSURE DROP |  | TEMPERATURE |
| 2000 CFM | 70 - 80 Pa | 450 Pa |  | AMBIENT |
| TEST DATA |  |  |  |  |
| TEST AIRFLOW | AIR VELOCITY |  | AIR TEMPERATURE |  |
| 500 FPM | 25 °C |  | 25 °C |  |
| TEST RESULT |  |  |  |  |
| INITIAL PRESSURE DROP (Pa) | EFFCIENCY |  | FILTER CLASS |  |
| 70 ± 5 % | 99% DOWN TO 3 MICRON |  | EU 07 |  |
| TEST TYPE: BS EN 779 |  |  |  |  |
| INSPECTED BY For Queries Related To TC Please Contact – quality@airfil.in Authorised Signatory |  |  |  |  |